## Slide 1
Your Optical Fiber Solutions Partner®
All Rights Reserved, Copyright © OFS Fitel, LLC 2017
My cable – the inside story
Mark Boxer
Applications Engineering Manager
OFS

## Slide 2: Agenda
Fiber property refresher
  The cable protects the fiber
Cable anatomy
  Primarily for electric coop and municipal builds
  Trunk/distribution versus drop cables
Pros and cons of lashed versus ADSS cables and more detailed ADSS information

## Slide 3: Different fiber types do different jobs
G.652.D/G.657A1
Network core and drops
Cabinets, boxes,
closures
G.652.D/G.657A2
G.657B3
In homes and buildings

## Slide 4: ITU-T G.657 Bend Loss Insensitive SM Fiber
Minimum design radius | ITU-T G.657 Fiber Standard
10 mm Bend Challenged OSP Cable | G.657A1
7.5 mm Most Connectivity Applications | G.657A2
5.0 mm In Home/MDU Drop | G.657B3

## Slide 5
Fiber strain
Limiting fiber strain drives all mechanical reliability calculations
< 0.2% long-term strain targeted for negligible crack growth
  Higher allowable for short periods of time
Serves as cable tension limitation –
  Maximum Rated Cable Load (for ADSS)
  Max Installation Tension (for duct/underground cables)
Fiber has become well known for outstanding reliability – due to this limitation
Tension
< 0.2% strain

## Slide 6
Outside Plant Cable Anatomy
Most often “loose tube” cable structure
  Fibers loose in buffer tubes
    Handles stress/strain and temperature fluctuations and climatic extremes
  Also available in ribbons
  Fibers and buffers are color coded
Underground applications
  Direct Buried – typically armored
  Duct cable
Aerial applications
  Lashed to a messenger
  Self-supporting (ADSS, All-Dielectric, Self-Supporting)
Buffer tube
Fiber
Loose buffer tube structure
Flat ribbon
Rollable ribbon

## Slide 7
Outside Plant Cable Anatomy

## Slide 8
Outside Plant Cable Anatomy

## Slide 9
Differences between ADSS and Loose Tube Duct Cable Applications
Lashed
Uses metallic strand to support cables
Used for legacy copper, coax cables
ADSS
Often used for new builds with no strand
Self-supporting cable
ADSS
Lashed

## Slide 10
Differences between ADSS and Loose Tube Duct Cables
Loose tube duct cables, lashed to a messenger wire
  Not self-supporting
  Typical 600 pound pulling tension short term
  Ice/wind load absorbed by the strand
  More strain expected at installation
ADSS, (All-Dielectric, Self-Supporting)
  Self-supporting – designed for span lengths and ice and wind loads
  Least strain at installation
  More strain upon loading – typically higher “MRCL” (Maximum rated cable load”

## Slide 11
Differences between ADSS and Loose Tube Duct Cables
Tube thickness and free space are important
  Tube wall thickness
    Higher crush resistance
  Free space and excess fiber length
    Higher margin before fiber strain
OFS ADSS tube
Competitor ADSS and standard loose tube
Thicker wall
Roughly to scale
More free space
Not to scale

## Slide 12
Differences between ADSS and Loose Tube Duct Cables
EFL (Excess Fiber Length)
  Sometimes different between ADSS and loose tube cables
  Balance is needed
    More fiber enables more stretch before fiber strain
    Too much fiber can induce attenuation issues
ADSS tube and EFL – not to scale
Loose tube duct cable tube and EFL – not to scale

## Slide 13
Stranding angles are important
  Steeper angles enable more stretch before fiber strain occurs
  Uses more fiber
Differences between ADSS and Loose Tube Duct Cables
Stranding angle
Shallower angle
Steeper angle

## Slide 14
Differences between ADSS and Loose Tube Duct Cables
Duct cables – Often use glass rovings
Short span ADSS cables – Often use aramid yarns for strength and to limit stretch
Long span ADSS cables – Often uses more aramid and 2 jackets
Amounts and types of strength member (fiberglass or aramid) are important to control stretch of the cable

## Slide 15
The importance of gel-free
Lighter
Lower tensions
Easier to use
Lower labor to prep

## Slide 16: Cable choice depends on the application
OFS expects long-term reliability for either cable type to be similar.
Solutions can be mixed and matched as needed.
Often better choice when going to new areas
Lower make-ready and installation costs
Less clean drop management
Often faster installation
ADSS
Lashed cable
Typically more expensive unless strand is available
Good choice for higher customer density areas and more ground clearance
Higher make-ready costs and slower initial deployment
Cleaner drop management

## Slide 17: Why ADSS for FTTH?
Fast and inexpensive installation
No need to lash
Lower tensions – possibly less guying
Little to no maintenance
No bonding or grounding
Can place in supply zone
  Reduces make-ready
Often the best choice for FTTH when building to new areas

## Slide 18: Where to use lashed cables
“No brainer” if a strand is already installed
Higher density areas (reduces pole attachments for drops)

## Slide 19: A typical ADSS network
PowerGuide ShortSpan DT and hardware
SlimBox Drop Terminal and splitter
PowerGuide TTH and hardware
SlimBox CSP and EZ Bend to the ONT

## Slide 20: ADSS installed cost is typically significantly less expensive
Installation typically significantly less expensive
  Install 1 cable versus 2
  Fewer trips up the pole
  $0.20-$0.30/foot less expensive
Typically much faster
  1-2 km/day are not unusual
  Depends on Right of way
Lower tensions – possibly less guying
  Assume roughly $0.08/foot
No maintenance
No bonding or grounding
Can place in supply zone
  Reduces make-ready, up to $0.25/foot
The best choice for FTTH when building to new areas
Cable and installation costs for 50,000’ 24 fiber network
Chart: 
| ADSS: | Lashed Loose Tube
Cable Total | 0.11956 | 0.11125
Material Total | 0.031096 | 0.1114
Labor Total | 0.55415 | 0.69269
Make Ready | 0 | 0.046179
Guying | 0 | 0.038483

## Slide 21: How does ADSS work?
Si
Sl
ɛ
(Strain)
σ (Stress)
x
x
x
x
After installation
Designed loading
Fiber strain begins
Max Rated Cable Load (MRCL)
Fibers break
Cable breaks
x
x

## Slide 22: Required Design Information
Si
Si = sag initial (no load)
span
Fiber count
Worse case environmental loading conditions
    Ice thickness (radial or rime), wind
    Temperature, safety factors
Maximum span – not ruling span
Installation Sag Percent
  Installation sag as a percent of the span. Assumed to be 1.5% if not specified.
  Loaded sag % (if required)
Line voltage
Sl
Sl = sag loaded
Loaded case shown exaggerated*

## Slide 23: Ice and wind loading
Ice loading with ADSS
Round, typically no galloping
Ice loading with lashed or figure 8, Airplane wing shape Possible galloping

## Slide 24: ADSS cable reliability – main components
Fiber
  Following recommended installation tensions limits fiber strain
  <0.2% strain corresponds to 1% crack growth
  Corresponds to 40 year lifetime
  No known upper lifetime limit
Aramid
  No known fatigue mechanism similar to those in metals
All materials
  Strain is limited to the “elastic” range of the curve, no plastic deformation
Inner/Outer polyethylene jacket
  Bell Labs/OFS work on polyethylene began in 1947
  Deep understanding of various reactions with UV, aging, etc
  View from technical community
  “We don’t know when jackets with 2.6% N110 black will degrade … they have not existed long enough for us to find out yet.”
  “Current modern black PE jackets for aerial optical cable will almost certainly be fine long after we’re all dead.”

## Slide 25
Squirrels – ADSS versus lashed armored cables
Cables need to last for decades
Squirrels will eat through either dielectric or armored cables
  Armored cables may take a little longer, but will eventually also need to be replaced
    Armored cables have their own concerns – specifically bonding/grounding, and lightning
  OFS is familiar with various additives used for “squirrel resistance”.
    We are skeptical of their long-term performance.
OFS’ position for coops
  The best defense against squirrels is an effective tree-trimming program
  The benefits of dielectric cables outweigh the limited additional time provided by using armored cables

## Slide 26: Other ADSS performance notes
ADSS has small coefficient of thermal expansion vs metal cables
ADSS has small creep vs metal cables

## Slide 27: Typical OFS ADSS options
Main trunk cables and ultra-long drops
  PowerGuide DT, Gel-Free ADSS
  Lite tension formed wire deadends and tangent clamps
Branch and longer span drop cables
  PowerGuide TTH “To the home”, 9.0 mm
  Up to 300-400’ spans, dependent upon sag/tension/loading
  PLP 2888 series deadends for shorter spans
  Lite tension deadends for longer spans
Shorter drops
  Mini LT flat drop
  Roughly 250’ spans, dependent upon sag/tension/loading
  Uses very inexpensive wedge clamp

## Slide 28: PowerGuide® DT Short Span ADSS Cable
Fiber counts to 144
Span lengths 500 feet (150m) or longer
  Depending upon loading and sag
World’s first fully qualified gel-free ADSS cable
Qualified to Telcordia GR 20 Core, IEEE 1222, RUS PE 90
  OFS deeply involved with standards-setting process
Ideally suited for short span distribution line applications

## Slide 29: PowerGuide® TTH ADSS Cable
  TTH - “To the Home”
  Max fiber count, 30
  6 fibers per tube – 2.0mm Tubes
  Typical span lengths to 80 meters
  Single jacket for drop type applications
  Very inexpensive hardware

## Slide 30
Mini LT Drop Cable
Flat drop
Typically uses Belden/PPC drop deadend
PLP has formed wire deadend
MRCL – 300 lbs

## Slide 31: Terminals and closures
SlimBox Drop Terminal
  Spliced or pre-connectorized drops
  Holds splitters
  Designed specifically for ADSS drop applications
  Cost effective
Standard fiber optic closure
  For longer span applications

## Slide 32: More ADSS terminal and closure detail
Common mounting methods
  Pole mounting
  Deadend mounting
    If deadend mounting, formed wire hardware is typically used
OFS SlimBox Drop Terminal mounted on a pole
PLP closures attached to a deadend. Photos courtesy PLP

## Slide 33: Splice and Slack Storage (Cable Mount)
ADSS snowshoes often used
Storage is done on either side of the pole (instead of in the span)
OFS provides a rule of thumb of 150’ per pole (37.5’ x 2, each side)

## Slide 34
24”
30”
Minimum Dimension Requirements
30” - Height
24” - Width
12” - Depth
Splice and Cable Storage (Pole Mount)
Photo courtesy of Telenco

## Slide 35
Leave Sufficient Cable
For Splicing Purposes
Splice and Cable Storage (Buried)

## Slide 36: Managing multiple drops on a span
OFS recommendation is a separate pole attachment point for each drop
For aesthetic and/or make-ready concerns
  Mini-LT flat drop may be tie-wrapped to the main ADSS cable at undefined intervals.
  Not completely risk free
  Contact OFS to discuss
OFS white paper, “Using ADSS cable in distribution applications - Storage and cable drop management” available for guidance

## Slide 37: Summary
The main purpose of the cable is to protect the fiber
  Using appropriate fiber and managing strain is critical to long term performance
Loose tube duct and ADSS cables are designed for different applications
  OFS expects similar reliability
  Many pros and cons to consider
Multiple ways of deploying cables
  Weigh various factors when deploying
OFS can assist in assessing the best solution for the application

## Slide 38: Questions?
Mark Boxer
Applications Engineering Manager
OFS
mboxer@ofsoptics.com
252 495-4131